| # | Disturbance | Main phenomenon | Main standard | IEEE-referenced characteristic | Proposed simulation duration | Proposed cycles | Main parameter | How generated | How independently analyzed | Final classification |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Normal | Nominal sinusoidal voltage | IEEE 1159-2019 framework | No qualifying PQ disturbance | 200 ms | 10 | f0=50Hz | Pure sine wave | RMS + frequency + THD + waveform check | Normal |
| 2 | Voltage Sag | Temporary reduction in RMS voltage | IEEE 1159-2019 | 0.1–0.9 pu; instantaneous 0.5–30 cycles | 2–10 cycles recommended | 2–10 | Sag magnitude | Reduce sinusoidal amplitude during event | Windowed RMS + duration | Sag |
| 3 | Voltage Swell | Temporary increase in RMS voltage | IEEE 1159-2019 | 1.1–1.8 pu instantaneous; duration categories depend on event class | 2–10 cycles recommended | 2–10 | Swell magnitude | Increase sinusoidal amplitude during event | Windowed RMS + duration | Swell |
| 4 | Interruption | Voltage falls to very low level | IEEE 1159-2019 | <0.1 pu; 0.5 cycle–3 s for momentary interruption | 1–5 cycles recommended | 1–5 | Residual voltage | Reduce voltage close to zero | Windowed RMS | Interruption |
| 5 | Harmonics | Integer-multiple frequency components | IEEE 1159 + IEEE 519-2022 | Steady-state harmonic distortion; IEEE 519 limits apply at PCC | Entire record | 10 | Harmonic amplitudes + THD | Add H3/H5/H7/H9/H11 | FFT + THD + harmonic spectrum | Harmonics |
| 6 | Oscillatory Transient | Short high-frequency oscillation | IEEE 1159-2019 | Oscillatory transient characterized by frequency/duration; your 5-kHz sampling restricts simulated frequency range | ~5–30 ms recommended | 0.25–1.5 fundamental cycles | ftrans, damping τ | Damped sinusoid | STFT/FFT + transient energy + damping | Oscillatory transient |
| 7 | Flicker / voltage fluctuation | Periodic voltage-amplitude variation | IEEE 1453-2022 | Voltage fluctuation/flicker; Pst/Plt are IEEE 1453 indices | Longer than 200 ms for true flicker assessment; 200 ms only for simplified waveform/ML simulation | Depends on fm | Modulation depth + fm | Amplitude-modulated sine | Envelope analysis; proper flicker assessment requires appropriate flickermeter methodology | Flicker |
| 8 | Notch | Repetitive localized waveform distortion | IEEE 1159-2019 | Waveform-distortion phenomenon | Entire 200-ms record | Repeated over 10 cycles | Depth + width + repetition | Subtract narrow pulse/notch from sinusoid | Ideal-vs-actual waveform error + width/depth/periodicity | Notch |

The important distinction is:

- IEEE 1159-2019 → primary classification/taxonomy of PQ phenomena.

- IEEE 519-2022 → harmonic-control/distortion requirements at the PCC; it supplements the harmonic class rather than replacing 1159.

- IEEE 1453-2022 → voltage fluctuations/flicker and RVC assessment.

- IEEE 1159.3-2025 → PQ data interchange/metadata, not the classification rules.

BASIC

| Class | Step 1: What is measured? | Step 2: What is calculated? | Step 3: What is checked? | Final class |
| --- | --- | --- | --- | --- |
| Normal | Voltage waveform | RMS, frequency, THD, spectrum | No qualifying disturbance | NORMAL |
| Sag | Voltage | Windowed RMS | RMS = 0.1–0.9 pu for appropriate duration | SAG |
| Swell | Voltage | Windowed RMS | RMS = 1.1–1.8 pu for appropriate duration | SWELL |
| Interruption | Voltage | Windowed RMS | RMS <0.1 pu for qualifying duration | INTERRUPTION |
| Harmonics | Voltage | FFT + THD | Integer-multiple spectral components | HARMONICS |
| Oscillatory transient | Voltage | STFT/FFT + transient envelope | Temporary oscillatory HF component | TRANSIENT |
| Flicker | Voltage | Envelope + flicker analysis | Voltage fluctuation / flicker characteristics | FLICKER |
| Notch | Voltage | Ideal-vs-actual waveform error | Repetitive localized notches | NOTCH |

According to each Disturbance

EXACTLY HOW SAG IS CLASSIFIED

| Parameter | Rule |
| --- | --- |
| Fundamental | 50 Hz |
| Cycle | 20 ms |
| RMS calculation | Moving/windowed RMS |
| Normal reference | 1.0 pu RMS reference |
| Sag region | 0.1–0.9 pu |
| Instantaneous sag duration | 0.5–30 cycles |
| Time equivalent | 10–600 ms at 50 Hz |
| Momentary sag | 30 cycles–3 s |
| Temporary sag | >3 s–1 min |
| Detection | RMS falls below nominal and enters sag region |
| Start | First window satisfying condition |
| End | First return outside sag condition after event |
| Duration | tend-tstart |
| Cycles | Duration × 50 |
| Magnitude | Minimum/representative RMS during event |
| Final decision | Magnitude + duration |
| Standard | IEEE 1159-2019 |

The 0.5–30-cycle instantaneous range and 0.1–0.9 pu magnitude are reproduced from the IEEE 1159-2019 classification table.

EXACTLY HOW SWELL IS CLASSIFIED

| Parameter | Rule |
| --- | --- |
| Fundamental | 50 Hz |
| Cycle | 20 ms |
| RMS analysis | Moving/windowed RMS |
| Swell region | 1.1–1.8 pu |
| Instantaneous duration | 0.5–30 cycles |
| Time | 10–600 ms |
| Momentary | 30 cycles–3 s |
| Momentary magnitude | 1.1–1.4 pu |
| Temporary | >3 s–1 min |
| Temporary magnitude | 1.1–1.2 pu |
| Start | RMS enters swell region |
| End | RMS returns from swell region |
| Duration | End − start |
| Classification | Magnitude + duration |
| Standard | IEEE 1159-2019 |

EXACTLY HOW INTERRUPTION IS CLASSIFIED

| Parameter | Rule |
| --- | --- |
| Fundamental | 50 Hz |
| Residual RMS | <0.1 pu |
| Momentary interruption | 0.5 cycle–3 s |
| At 50 Hz | 10 ms–3 s |
| Temporary interruption | >3 s–1 min |
| Sustained interruption | >1 min |
| Detection | RMS falls below 0.1 pu |
| Duration | Time below threshold |
| Class | Interruption |
| Standard | IEEE 1159-2019 |

EXACTLY HOW HARMONICS ARE CLASSIFIED

| Parameter | Analysis |
| --- | --- |
| Fundamental | 50 Hz |
| FFT | Required |
| H2 | 100 Hz |
| H3 | 150 Hz |
| H5 | 250 Hz |
| H7 | 350 Hz |
| H9 | 450 Hz |
| H11 | 550 Hz |
| Harmonic frequency | nf0 |
| THD | Calculate from harmonic components |
| Individual harmonic magnitude | Calculate |
| Harmonic phase | Optional but useful metadata |
| Duration | Steady-state / entire record in your synthetic class |
| IEEE 1159 role | Identifies harmonics as waveform distortion |
| IEEE 519 role | Harmonic-control/distortion requirements, especially at PCC |
| Classification | Significant integer-multiple spectral content |
| Important | Do not define "THD > 5%" as an IEEE 519 classification unless the exact application/limit supports it |
| Standard | IEEE 1159-2019 + IEEE 519-2022 |

IEEE 519-2022 explicitly addresses steady-state voltage/current distortion and the PCC; it is not a general classifier for all waveform types.

EXACTLY HOW OSCILLATORY TRANSIENT IS CLASSIFIED

| Parameter | Low-frequency oscillatory transient |
| --- | --- |
| IEEE category | 1.2.1 |
| Spectral content | <5 kHz |
| Typical duration | 0.3–50 ms |
| Typical magnitude | 0–4 pu |
| Your sampling frequency | 5 kHz |
| Your Nyquist | 2.5 kHz |
| Consequence | Your simulation cannot represent the complete <5-kHz band |
| Recommended simulation | Restrict to e.g. 300–2000 Hz |
| Model | Damped sinusoid |
| Detection | STFT / FFT |
| Transient energy | Calculate |
| Transient frequency | Calculate |
| Start time | Detect |
| End time | Detect |
| Damping | Estimate |
| Classification | Temporary oscillatory HF component |
| Standard | IEEE 1159-2019 |

The published IEEE 1159-2019 table identifies low-frequency oscillatory transients as below 5 kHz with a typical 0.3–50 ms duration; medium- and high-frequency categories extend far beyond what your current 5-kHz sampling can represent.

Therefore, this is a real issue in your current plan.

You should either:

A. keep 5 kHz and explicitly restrict your synthetic transient class to a representable sub-band, or

B. increase the sampling frequency.

For your current project, A is much simpler.

EXACTLY HOW FLICKER IS CLASSIFIED

| Parameter | Flicker |
| --- | --- |
| IEEE 1159 category | Voltage fluctuations |
| Typical modulation frequency | <25 Hz in 1159 taxonomy |
| Standard | IEEE 1159-2019 + IEEE 1453-2022 |
| IEEE 1453 purpose | Measurement and limits of voltage fluctuations and associated light flicker |
| Measurement | Flickermeter methodology |
| Short-term index | Pst |
| Long-term index | Plt |
| PCC assessment | Yes |
| Your simple waveform | Amplitude-modulated 50-Hz waveform |
| Example | vt=Vm1+msin⁡2πfmtsin⁡2π50t |
| Analysis | Envelope extraction |
| Calculate | Modulation depth |
| Calculate | Modulation frequency |
| True IEEE flicker assessment | Requires appropriate flickermeter/observation methodology |
| 200-ms record | Not sufficient to claim a full Pst/Plt assessment |
| ML simulation | Can use shorter segments as synthetic examples |
| Standard-compliance claim | Must not be based only on your simple modulation equation |

IEEE 1453-2022 specifically defines the Pst and Plt indices and describes flicker measurement using an IEC 61000-4-15 flickermeter.

EXACTLY HOW NOTCH IS CLASSIFIED

| Parameter | Notch |
| --- | --- |
| IEEE category | Waveform distortion |
| IEEE 1159 class | Notching |
| Duration | Steady-state/repetitive |
| Fundamental | 50 Hz |
| Record | 200 ms |
| Fundamental cycles | 10 |
| Generation | Remove a narrow localized section of waveform |
| Main parameter | Notch depth |
| Main parameter | Notch width |
| Main parameter | Repetition |
| Main parameter | Phase/location |
| Analysis | Compare actual waveform with ideal sine |
| Error | et=videal-vactual |
| Detect | Repeated narrow deviations |
| FFT | Useful but not sufficient alone |
| Time-domain analysis | Essential |
| IEEE numerical threshold | Do not invent one |
| Classification | Repetitive waveform notches |
| Standard | IEEE 1159-2019 |