Power Quality Monitoring and Disturbance Classification System Using Machine Learning

1. INTRODUCTION

Modern electrical power systems are increasingly affected by power quality disturbances caused by nonlinear loads, switching operations, faults, renewable energy integration, and rapid changes in electrical loads. These disturbances can reduce equipment efficiency, cause malfunctioning of sensitive electronic devices, increase energy losses, and affect the overall reliability of the electrical system.

Traditional power quality analyzers can monitor electrical parameters such as voltage, frequency, and harmonic distortion. However, identifying the type of disturbance and interpreting large amounts of electrical data often requires manual analysis or expensive commercial equipment.

Machine Learning provides an opportunity to automate the identification of power quality disturbances. By analyzing electrical parameters extracted from voltage waveforms, a trained machine learning model can classify disturbances such as voltage sag, voltage swell, harmonic distortion, and other abnormal conditions.

The proposed project aims to develop a real-time power quality monitoring device capable of monitoring an electrical system continuously and identifying power quality disturbances using Machine Learning.

The system will consist of a hardware monitoring unit for voltage measurement and waveform acquisition, a processing unit for feature extraction, and a machine learning-based classification system for identifying the disturbance.

The initial prototype will be developed using a safe low-voltage 12V AC system. The architecture will be designed so that it can later be adapted for monitoring higher-voltage electrical systems using appropriate isolation and sensing circuits.

2. PROBLEM STATEMENT

Power quality disturbances can occur in electrical systems due to various reasons, including sudden changes in load, nonlinear electronic equipment, switching operations, and faults.

Common disturbances include:

- Voltage Sag

- Voltage Swell

- Harmonics

- Flicker

- Transients

- Frequency Variations

These disturbances may affect:

- Electrical motors

- Industrial equipment

- Electronic devices

- Control systems

- Sensitive loads

- Communication systems

Existing power quality analyzers are often expensive and require manual interpretation of recorded data.

Therefore, there is a need for a low-cost intelligent monitoring system capable of:

- Monitoring electrical parameters continuously.

- Detecting abnormal power quality conditions.

- Extracting important waveform features.

- Automatically classifying disturbances using Machine Learning.

- Providing real-time monitoring and visualization.

- Securely transmitting or storing monitoring data.

3. AIM OF THE PROJECT

The aim of this project is to develop an AI-based real-time power quality monitoring and disturbance classification system capable of monitoring an electrical system, extracting power quality parameters, and automatically identifying disturbances using Machine Learning.

4. OBJECTIVES

The major objectives of the project are:

- To design a hardware-based power quality monitoring unit.

- To continuously monitor the voltage waveform of an electrical system.

- To acquire real-time electrical waveform data using sensors and an Analog-to-Digital Converter.

- To calculate important power quality parameters such as:

  - RMS Voltage

  - Peak Voltage

  - Crest Factor

  - Frequency

  - Total Harmonic Distortion

- To develop a Machine Learning model for power quality disturbance classification.

- To classify disturbances such as:

  - Normal Condition

  - Voltage Sag

  - Voltage Swell

  - Harmonic Distortion

- To display real-time electrical parameters and disturbance classification results.

- To implement data logging for monitoring and analysis.

- To incorporate basic cybersecurity mechanisms for secure monitoring and communication.

- To develop the prototype using a safe 12V AC electrical system.

5. SCOPE OF THE PROJECT

The project focuses on developing a prototype of a real-time power quality analyzer.

The initial prototype will monitor a low-voltage 12V AC system to ensure safe development and testing.

The system will measure the electrical waveform and calculate power quality parameters.

The Machine Learning system will initially focus on the following disturbance categories:

Primary Classification Categories

- Normal

- Voltage Sag

- Voltage Swell

- Harmonic Distortion

Additional disturbances such as flicker and transients may be investigated in future development.

The architecture will be scalable for future applications involving:

- Single-phase systems

- 230V AC systems

- Industrial power systems

- Three-phase systems

However, direct high-voltage monitoring will require appropriate certified voltage transformers, isolation, protection, and safety practices.

6. PROPOSED SYSTEM

The proposed system consists of three major sections:

A. Electrical Monitoring Section

Responsible for monitoring the electrical waveform.

B. Data Processing Section

Responsible for converting and processing the acquired waveform.

C. Machine Learning Classification Section

Responsible for identifying the type of power quality disturbance.

7. OVERALL SYSTEM ARCHITECTURE

ELECTRICAL SYSTEM

│

▼

12V AC SIGNAL

│

▼

VOLTAGE SENSING UNIT

│

▼

SIGNAL CONDITIONING

│

▼

EXTERNAL ADC

│

▼

ESP32

│

┌────────────┼─────────────┐

│            │             │

▼            ▼             ▼

FEATURE         DISPLAY       DATA

EXTRACTION                    TRANSMISSION

│                          │

▼                          ▼

MACHINE LEARNING              DASHBOARD

│

▼

DISTURBANCE CLASSIFICATION

│

┌───────┼────────┬───────────┐

▼       ▼        ▼           ▼

NORMAL    SAG     SWELL     HARMONICS

8. WORKING PRINCIPLE

The proposed system works in the following sequence.

Step 1: Voltage Monitoring

The electrical voltage waveform is monitored using an isolated voltage sensing arrangement.

The initial system will monitor a 12V AC waveform.

Step 2: Signal Conditioning

The measured signal is conditioned to make it suitable for the Analog-to-Digital Converter.

Signal conditioning may include:

- Voltage scaling

- DC biasing

- Filtering

- Input protection

Step 3: Data Acquisition

The conditioned analog waveform is converted into digital samples using an external ADC.

The digital samples are transmitted to the ESP32.

Step 4: Feature Extraction

The ESP32 or connected processing system calculates important power quality features.

These include:

RMS Voltage

Peak Voltage

Crest Factor

Frequency

THD

Duration

Step 5: Machine Learning Classification

The extracted features are provided to the trained Machine Learning model.

The ML model analyzes the features and determines the disturbance category.

Example:

INPUT FEATURES

V_RMS = 0.65 pu

THD = 4%

Frequency = 50 Hz

Duration = 200 ms

↓

MACHINE LEARNING MODEL

↓

OUTPUT

VOLTAGE SAG

Step 6: Display and Monitoring

The classification result and electrical parameters are displayed locally and/or on a monitoring dashboard.

9. POWER QUALITY DISTURBANCES

9.1 Normal Condition

Under normal conditions, the voltage waveform maintains its rated magnitude and frequency.

For the prototype:

Voltage ≈ Rated Voltage

Frequency ≈ 50 Hz

THD = Within acceptable limits

The Machine Learning model should classify this condition as:

NORMAL

9.2 Voltage Sag

A voltage sag is a temporary reduction in RMS voltage.

Possible causes include:

- Starting of large motors

- Short circuits

- Sudden increase in load

- Fault conditions

Example:

NORMAL VOLTAGE

/‾‾\      /‾‾\

_____/    \____/    \____

VOLTAGE SAG

/‾\      /‾\

_____/   \____/   \____

The primary feature indicating a sag is:

Reduced RMS Voltage

9.3 Voltage Swell

A voltage swell is a temporary increase in RMS voltage.

Possible causes include:

- Sudden removal of heavy loads

- Switching operations

- Electrical faults

Example:

NORMAL

/‾‾\      /‾‾\

____/    \____/    \____

SWELL

/‾‾‾‾\

______/      \______

The primary feature indicating a swell is:

Increased RMS Voltage

9.4 Harmonics

Harmonics occur when the voltage waveform deviates from a pure sinusoidal waveform.

Common sources include:

- Rectifiers

- Variable frequency drives

- SMPS

- Computers

- LED drivers

- Nonlinear loads

A harmonic waveform may look distorted.

PURE SINE WAVE

/‾‾\

______/    \______

DISTORTED WAVE

/‾\_/‾\

_____/       \____

The major parameter used to analyze harmonics is:

Total Harmonic Distortion (THD)

10. POWER QUALITY PARAMETERS

10.1 RMS Voltage

The RMS value represents the effective value of the AC voltage.

VRMS=1Nn=1NVn2

RMS voltage is important for detecting:

- Voltage Sag

- Voltage Swell

- Interruptions

10.2 Peak Voltage

Peak voltage represents the maximum voltage value of the waveform.

VPeak=Maximum∣V∣

It helps identify:

- Amplitude variations

- Voltage abnormalities

10.3 Crest Factor

The Crest Factor is calculated as:

Crest Factor=VPeakVRMS

A normal sinusoidal waveform has a theoretical Crest Factor of approximately:

2

Changes in Crest Factor may indicate waveform distortion.

10.4 Frequency

The system frequency is expected to be approximately:

50 Hz

Frequency can be calculated using:

- Zero crossing detection

- FFT analysis

The proposed system will monitor frequency variations in the electrical waveform.

10.5 Total Harmonic Distortion

THD represents the amount of harmonic distortion present in the waveform.

THD=V22+V32+V42+...V1×100

Where:

- V1= Fundamental voltage

- V2,V3,V4= Harmonic components

THD will be calculated using frequency-domain analysis such as FFT.

11. MACHINE LEARNING SYSTEM

The Machine Learning system will use historical and labelled power quality data to learn the characteristics of different disturbances.

The available dataset contains features such as:

- RMS Voltage

- Peak Voltage

- Crest Factor

- THD Percentage

- Duration

- Dominant Frequency

- System Frequency

- Signal-to-Noise Ratio

The output label represents the type of power quality disturbance.

12. MACHINE LEARNING WORKFLOW

DATASET

│

▼

DATA PREPROCESSING

│

▼

FEATURE SELECTION

│

▼

TRAIN / TEST SPLIT

│

▼

MACHINE LEARNING MODELS

│

┌─────────┼─────────┐

▼         ▼         ▼

Random     Decision      SVM

Forest      Tree

│         │         │

└─────────┼─────────┘

│

▼

PERFORMANCE COMPARISON

│

▼

SELECT BEST MODEL

│

▼

REAL-TIME DEPLOYMENT

13. PROPOSED MACHINE LEARNING ALGORITHMS

The following algorithms will be evaluated.

13.1 Random Forest

Random Forest is recommended as the primary Machine Learning model because:

- It works effectively with tabular data.

- It can handle multiple features.

- It is relatively easy to interpret.

- It provides good classification performance.

- It can be optimized for deployment.

13.2 Decision Tree

Decision Tree classification will be used as a baseline model.

Advantages:

- Simple

- Easy to understand

- Easy to explain during viva

13.3 Support Vector Machine

SVM may be used for comparison with other classification algorithms.

14. DATASET

The project uses an available labelled power quality dataset for Machine Learning model development.

The dataset contains approximately:

10,000 samples

The available features include:

| Feature | Description |
| --- | --- |
| V_rms_pu | RMS Voltage in per unit |
| V_peak_pu | Peak Voltage |
| Crest_Factor | Ratio of peak to RMS voltage |
| THD_percent | Total Harmonic Distortion |
| Duration_ms | Duration of disturbance |
| Dominant_Freq_Hz | Dominant frequency component |
| Freq_Hz | System frequency |
| SNR_dB | Signal-to-noise ratio |
| Label | Disturbance classification |

The dataset includes disturbance labels such as:

- Sag

- Swell

- Harmonics

- Flicker

- Transient

The final selected categories for the first hardware prototype will depend on successful correlation between the live measured data and dataset features.

15. IMPORTANT DATASET AND HARDWARE INTEGRATION

The Machine Learning dataset contains processed electrical features.

However, the hardware system measures the actual waveform.

Therefore, the following process is necessary:

LIVE VOLTAGE WAVEFORM

│

▼

DIGITAL SAMPLING

│

▼

FEATURE EXTRACTION

│

▼

FEATURE NORMALIZATION

│

▼

SAME FORMAT AS DATASET

│

▼

MACHINE LEARNING MODEL

│

▼

DISTURBANCE CLASSIFICATION

This is one of the most important parts of the project.

The features calculated from live hardware must be compatible with the features used during ML training.

16. HARDWARE SYSTEM

The proposed hardware monitoring unit will include the following sections.

16.1 Voltage Sensing Unit

The voltage sensing unit measures the electrical voltage waveform.

For the prototype, the system will monitor:

12V AC

The sensing arrangement must provide electrical isolation and safe voltage scaling.

The future version can use:

- Potential Transformer

- Isolated voltage transducer

- Certified voltage measurement module

for higher voltage systems.

16.2 Signal Conditioning Circuit

The sensor output may not directly match the ADC input range.

Therefore, a signal conditioning circuit will be used.

Functions include:

- Voltage scaling

- DC offset or biasing where required

- Noise filtering

- Overvoltage protection

16.3 Analog-to-Digital Converter

The ADC converts the analog voltage waveform into digital samples.

An external ADC is preferred for better accuracy.

The sampling frequency must be selected according to the disturbances being analyzed.

For the initial prototype, the system will focus on:

- RMS measurement

- Frequency measurement

- Basic harmonic analysis

The exact ADC and sampling architecture will be finalized after testing the dataset requirements.

16.4 ESP32 Microcontroller

The ESP32 will act as the primary embedded controller.

Its responsibilities include:

- Receiving sampled waveform data

- Performing basic calculations

- Communicating with the ML system

- Displaying data

- Wi-Fi communication

- Data transmission

Advantages:

- Low cost

- Built-in Wi-Fi

- Compact

- Easy programming

- Suitable for IoT applications

16.5 Display Unit

An OLED or LCD display can show:

VOLTAGE RMS

FREQUENCY

THD

SYSTEM STATUS

DISTURBANCE TYPE

Example:

POWER QUALITY ANALYZER

Voltage: 11.8 V

Frequency: 50.02 Hz

THD: 3.2 %

STATUS: NORMAL

16.6 Data Logging

The system may use:

- Micro SD Card

- Local database

- Computer storage

Data logging can store:

Timestamp

Voltage

Frequency

THD

Disturbance

Confidence

17. PROPOSED HARDWARE COMPONENTS

| Component | Purpose |
| --- | --- |
| ESP32 Development Board | Main controller |
| 12V AC Isolated Source | Prototype electrical system |
| Isolated Voltage Sensor | Voltage monitoring |
| Signal Conditioning Circuit | ADC signal preparation |
| External ADC | Waveform acquisition |
| OLED Display | Live parameter display |
| SD Card Module | Data storage |
| Power Supply | Hardware power |
| Fuse and Protection Circuit | System protection |
| Enclosure | Hardware safety |

18. CURRENT MONITORING – FUTURE OR OPTIONAL MODULE

Current monitoring can be added to improve the system.

Possible parameters include:

- RMS Current

- Active Power

- Reactive Power

- Apparent Power

- Power Factor

- Current THD

The future system architecture can be:

ELECTRICAL SYSTEM

│

┌───────┴────────┐

│                │

▼                ▼

VOLTAGE SENSOR     CURRENT SENSOR

│                │

└───────┬────────┘

│

▼

ADC

│

▼

ESP32

For the first working prototype, voltage monitoring should be prioritized.

19. REAL-TIME CLASSIFICATION ARCHITECTURE

LIVE ELECTRICAL SYSTEM

│

▼

VOLTAGE

WAVEFORM

│

▼

SAMPLING

│

▼

DIGITAL SIGNAL

│

▼

FEATURE EXTRACTION

│

┌───────────┼────────────┐

│           │            │

▼           ▼            ▼

RMS          THD       FREQUENCY

│

▼

FEATURE VECTOR

│

▼

MACHINE LEARNING

│

▼

DISTURBANCE RESULT

20. REAL-TIME DEPLOYMENT STRATEGY

For practical development, the project will initially use the following architecture:

VOLTAGE SENSOR

│

▼

ADC

│

▼

ESP32

│

▼

FEATURE EXTRACTION

│

▼

Wi-Fi / Serial Communication

│

▼

LAPTOP / RASPBERRY PI

│

▼

MACHINE LEARNING MODEL

│

▼

CLASSIFICATION RESULT

Why this approach is recommended?

It is:

- Easier to develop

- Easier to debug

- More reliable

- Suitable for real-time demonstration

After successful implementation, the ML model can potentially be optimized for embedded deployment.

21. FUTURE EMBEDDED ML ARCHITECTURE

The advanced version can perform classification directly on the device.

VOLTAGE SENSOR

│

▼

ADC

│

▼

ESP32

│

▼

FEATURE EXTRACTION

│

▼

TINY MACHINE LEARNING MODEL

│

▼

DISTURBANCE OUTPUT

22. CYBERSECURITY FEATURES

Since the proposed system may transmit electrical monitoring data over a network, cybersecurity is considered.

The project will implement practical security features.

22.1 User Authentication

Access to the monitoring dashboard will require authorized login credentials.

22.2 Device Authentication

Only registered monitoring devices should communicate with the authorized application or server.

22.3 Secure Communication

Where network transmission is used, encrypted communication such as TLS-based secure communication may be implemented.

22.4 Secure Data Access

The monitoring data will only be accessible to authorized users.

22.5 Firmware Protection

Future improvements may include:

- Secure Boot

- Signed Firmware

- Secure OTA Updates

These features can help prevent unauthorized modification of device firmware.

23. CYBERSECURITY ARCHITECTURE

POWER QUALITY ANALYZER

│

▼

DEVICE AUTHENTICATION

│

▼

ENCRYPTED COMMUNICATION

│

▼

AUTHORIZED SERVER

│

▼

USER LOGIN SYSTEM

│

▼

DASHBOARD

24. EXPECTED OUTPUT

The final system should display information such as:

---------------------------------

POWER QUALITY ANALYZER

Voltage RMS: 11.8 V

Frequency: 50.01 Hz

THD: 3.5 %

Crest Factor: 1.41

-------------------------------

AI CLASSIFICATION:

NORMAL

Confidence: 96%

---------------------------------

During a disturbance:

---------------------------------

⚠ DISTURBANCE DETECTED

Voltage RMS: 8.2 V

Frequency: 50 Hz

THD: 4 %

AI RESULT:

VOLTAGE SAG

Confidence: 94%

---------------------------------

25. PROJECT METHODOLOGY

The project will be implemented in the following stages.

Phase 1: Dataset Analysis

- Analyze dataset

- Identify features

- Identify disturbance labels

- Check data distribution

- Perform preprocessing

Phase 2: Machine Learning Development

- Data preprocessing

- Feature selection

- Train-test split

- Model training

- Model evaluation

- Performance comparison

- Model selection

Phase 3: Hardware Development

- Select voltage sensing method

- Design signal conditioning circuit

- Select ADC

- Configure ESP32

- Perform waveform acquisition

Phase 4: Signal Processing

Calculate:

- RMS

- Peak voltage

- Frequency

- Crest factor

- THD

Phase 5: Hardware and ML Integration

ESP32

│

▼

LIVE FEATURES

│

▼

ML MODEL

│

▼

CLASSIFICATION

Phase 6: Real-Time Visualization

Develop:

- OLED display

- PC dashboard

- Data visualization

Phase 7: Cybersecurity Implementation

Implement:

- Authentication

- Secure communication

- Access control

26. PROJECT INNOVATION

The proposed project combines three major technologies:

Electrical Engineering

Power Quality Monitoring

Signal Measurement

Electrical Waveform Analysis

Artificial Intelligence

Machine Learning

Feature-Based Classification

Real-Time Decision Making

IoT and Cybersecurity

Remote Monitoring

Secure Communication

Authorized Access

The combination of these technologies creates a practical smart power quality monitoring system.

27. ADVANTAGES OF THE PROPOSED SYSTEM

The proposed system provides:

- Real-time monitoring

- Automatic disturbance identification

- Reduced manual analysis

- Low-cost prototype

- Portable monitoring system

- Machine Learning-based decision making

- Data logging

- Remote monitoring capability

- Cybersecurity features

- Expandable architecture

28. APPLICATIONS

The proposed system can potentially be used in:

Industrial Systems

Monitoring:

- Motors

- Drives

- Industrial loads

Commercial Buildings

Monitoring:

- Electrical distribution

- Sensitive electronic equipment

Renewable Energy Systems

Monitoring:

- Solar inverter output

- Power conversion systems

Laboratories

Power quality experiments and research.

Smart Grid Systems

Distributed monitoring of electrical network quality.

Electrical Maintenance

Early identification of abnormal electrical conditions.

29. LIMITATIONS OF THE FIRST PROTOTYPE

The initial prototype will have certain limitations.

Low-Voltage Prototype

The initial testing system will operate on:

12V AC

Limited Disturbance Classes

The first working prototype will prioritize:

Normal

Sag

Swell

Harmonics

Transient Detection

Very fast transients may require:

- Higher sampling rate

- High-speed ADC

- Advanced signal processing

Therefore, transient classification may be treated as an advanced extension.

Dataset Dependency

The accuracy of the Machine Learning model depends on the similarity between:

TRAINING DATA

and:

LIVE HARDWARE DATA

Therefore, real hardware data collection and validation will be important.

30. FUTURE SCOPE

The system can be expanded in the future.

Possible improvements include:

Three-Phase Monitoring

Phase R

Phase Y

Phase B

Current Monitoring

Add:

- RMS Current

- Power

- Power Factor

- Current Harmonics

Advanced ML

Use:

- CNN

- LSTM

- Deep Learning

- Edge AI

Embedded AI

Deploy the ML model directly on:

ESP32

or a more capable embedded processor.

Cloud Monitoring

ANALYZER

│

▼

CLOUD SERVER

│

▼

REMOTE DASHBOARD

Predictive Maintenance

Use long-term power quality data to predict:

- Equipment failure

- Load abnormalities

- Power quality degradation

31. EXPECTED RESULTS

The expected system will:

- Successfully acquire live electrical waveform data.

- Calculate power quality parameters.

- Detect abnormal voltage conditions.

- Classify selected disturbances using Machine Learning.

- Display classification results in real time.

- Store disturbance events.

- Provide secure access to monitoring data.

32. FINAL PROJECT FLOW

STEP 1

LIVE ELECTRICAL SYSTEM

│

▼

STEP 2

VOLTAGE MONITORING

│

▼

STEP 3

SIGNAL CONDITIONING

│

▼

STEP 4

ADC SAMPLING

│

▼

STEP 5

ESP32 PROCESSING

│

▼

STEP 6

FEATURE EXTRACTION

RMS

THD

FREQUENCY

PEAK

CREST FACTOR

│

▼

STEP 7

MACHINE LEARNING MODEL

│

▼

STEP 8

CLASSIFICATION

NORMAL

SAG

SWELL

HARMONICS

│

▼

STEP 9

DISPLAY + DASHBOARD

│

▼

STEP 10

DATA LOGGING + SECURITY

33. CONCLUSION

The proposed AI-Based Real-Time Power Quality Monitoring and Disturbance Classification System aims to combine electrical power monitoring, signal processing, Machine Learning, IoT, and cybersecurity into a single intelligent monitoring platform.

The system will continuously monitor an electrical waveform and extract important power quality features such as RMS voltage, peak voltage, frequency, crest factor, and Total Harmonic Distortion.

These features will be analyzed using a trained Machine Learning model to automatically classify power quality disturbances.

The initial prototype will focus on a safe low-voltage 12V AC system and classify practical disturbances such as voltage sag, voltage swell, and harmonic distortion.

The system architecture will be scalable for future applications involving higher-voltage electrical systems, three-phase monitoring, current measurement, embedded AI, cloud connectivity, and predictive maintenance.

The project aims to demonstrate that Machine Learning can be integrated with real-time electrical monitoring hardware to create an intelligent, low-cost, and practical power quality analyzer.

⭐ MY RECOMMENDED FINAL PROJECT DEFINITION

For now, this should be our fixed project plan:

Input System

12V AC initially

Hardware

Voltage sensing + signal conditioning + external ADC + ESP32

Features

- RMS Voltage

- Peak Voltage

- Crest Factor

- Frequency

- THD

ML Classification

- Normal

- Sag

- Swell

- Harmonics

Output

- OLED Display

- Live Dashboard

- Data Logging

Security

- Authentication

- Secure communication

- Device access control